## Slide 1: Tractive Force Design with SewerGEMS
Tom Walski, Bentley Fellow

## Slide 2: Agenda
Goal – Self cleaning sewers
Tractive force basics
Implications
Tractive force in SewerGEMS/CAD
Application of tractive force design

## Slide 3: Importance of the Project – Public Health
http://neatorama.cachefly.net/images/2008-01/giant-blob-sewer.jpg
http://sfcitizen.com/blog/wp-content/uploads/2009/02/img_2191-copy.jpg

## Slide 4: Sewer Hydraulic Design
Move peak flow
  Slope
  Diameter
Move solids
  Slope
  Solids properties
  Flow

## Slide 5: Slope based approach
Chart: 10 State Standards
| 8 | 10 | 12 | 14 | 15 | 16 | 18 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 42
Slope, % | 0.4 | 0.28 | 0.22 | 0.17 | 0.15 | 0.14 | 0.12 | 0.1 | 0.08 | 0.067 | 0.058 | 0.052 | 0.046 | 0.041 | 0.037
Based on 2 ft/s when flowing full

## Slide 6: What is tractive force?
It is a shear “stress” not a force with units of force per area
parallel to the pipe wall (lb/ft2, Pascals)
Solid moves if
Actual tractive stress > Required tractive stress

## Slide 7: Required Tractive Stress
Based on 1 mm sand particle
Specific gravity = 2.7
Critical shear
  0.018 lb/ft2
  0.87 Pa
Raths and McAuley equation for critical shear
  Critical stress = 0.018 d0.277

## Slide 8: Actual Tractive Stress
Stress = γ S R
  γ = specific weight of fluid
  S = slope
  R = hydraulic radius
R = A/P
  A= cross section area
  P = wetter perimeter
Difficult to calculate manually

## Slide 9: Tractive Force Approach
ASCE MOP 60
WEF MOP FD-5

## Slide 10: Min Slope Small Sewers
8

## Slide 11: Comparing Approaches
8 in.
21 in.
42 in.

## Slide 12: Peak Flow Slope
Smin = 0.22

## Slide 13: Sizing and Slope
Chart: Min Flow, cfs
| 0.05 | 0.1 | 0.15000000000000024 | 0.2 | 0.25 | 0.30000000000000032 | 0.35000000000000031 | 0.40000000000000008 | 0.45 | 0.5
n=0.013 | 0.45284 | 0.30716 | 0.24477 | 0.20835 | 0.18388 | 0.16603 | 0.1523 | 0.14132 | 0.1323 | 0.12472
Variable | 0.51257 | 0.34456 | 0.27312 | 0.23162 | 0.20382 | 0.1836 | 0.16808 | 0.1557 | 0.14554 | 0.13701
10-state | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22

## Slide 14
Self-Cleansing Predictions vs. Observations

## Slide 15: Solve for slope to provide minimum required tractive stress
Pick
  Particle size
  Specific gravity
  Pipe roughness
  Diameter
Develop equation of Q vs. Smin
Smin = 0.00846 Q-0.56
  For 12 in. pipe, Q in cfs
Diameter, in. | a | b
6 | 0.000729 | 0.56
8 | 0.000776 | 0.56
12 | 0.000846 | 0.56
18 | 0.000922 | 0.56
24 | 0.000980 | 0.56
30 | 0.001028 | 0.56
36 | 0.001069 | 0.56
48 | 0.001143 | 0.566
60 | 0.001210 | 0.573
72 | 0.001271 | 0.576

## Slide 16: What flow to use?
Called Q min in WEF MOP FD-5
Need to reach this frequently to clean pipes
Qmin
  Not overall minimum
  More likely weekly or daily maximum flow
For very low flow (< 0.1 full)
  Flow arrives in pulses
  Use pulse flow

## Slide 17: Nature of Low Flows
Flow
Time
Flush
Bath tub
Average

## Slide 18: Steps to Use Tractive Stress
Select pipe based on capacity
  Size
  Slope
  Roughness
  Design particle
  Min flow
Determine minimum slope required
Generally need to adjust slope

## Slide 19: Design Differences Tractive Force vs. Slope
Actual TF slopes depend on flow rate
Milder slopes for small sewers
Potential savings in excavation in flat areas
Slightly steeper slopes for large sewers
Does not affect capacity aspect of pipe sizing
Smaller pipes give higher tractive force for same slope and flow

## Slide 20: Summary
Need to provide self-cleaning
SewerGEMS/SewerCAD can calculate tractive force
More theoretically correct way to determine slopes
Doesn’t apply to very low flow pipes
Easy check during design

## Slide 21: Tractive Force Design
Thank you