## Sheet1
CLA-VAL - Automatic control valves |  |  |  | VALVE SELECTED
VALVE SIZING GUIDE |  |  | Series: NGE |  | SIZE: | 200 | mm
ENTER THE FOLLOWING DATA:
Flow unit [1] l/s [2] m3h | [1 / 2] | 1
Pressure unit [1] bar [2] mhd | [1 / 2] | 2
MINIMUM Flow (Q min.) : | l/s | 70
MAXIMUM Flow (Q max.) : | l/s | 150
MINIMUM Inlet press (at Max.flow) | mhd | 35
MAXIMUM Inlet press (at min.flow) | mhd | 50
Desired Outlet Pressure | mhd | 5
SUGGESTED SERIES AND | Series NGE | 200
SIZES (mm) : | Series GE | 200 | 200
-----ENTER YOUR DISPLAY PREFERENCES BELOW-----
ENTER IN THE BOXES BELOW EITHER: ONE OF THE SUGGESTED
SERIES AND SIZES OR CHOOSE YOUR OWN SIZE TO DISPLAY
Body pattern [1] Globe [2] Angle | [1 / 2] | 1
Valve series: [1] GE or [2] NGE | [1 / 2] | 2
Valve size (mm): | NGE | 200
Valve Series selected : NGE | Min Flow | Max Flow
Valve %Cv | 25.0 | 66
Valve % Open | 34.9 | 62
Velocity [m/s] | 2.2 | 4.8
Headloss wide open valve [bar] | 0.28 | 1.27
Length of equivalent pipe [km] | 1.61 | 0.23
Stem lift [mm] | 15.00 | 26.70
Valve CV (l/s) |  | 133
Computed K | [-] | 11.2
Maximum Valve stem lift | [mm] | 43
Seat size | [mm] | 150